Alex MacFarlane Notes/Bullets for Sustainability

10.27.06

Heating

- 2 pipe fan coil condensing gas boiler

- 140º F supply water

Ventilating

- Naturally ventilated apartment for shoulder seasons

- Mechanically supplied fresh air from rooftop at low volumes

- Bathroom exhaust with heat recovery to preheat fresh air

- Remainder with infiltration

- Consider desiccant dehumidification

AC

- central non-electric or high efficiency chiller

- downsized to account for microclimate stuff

- oversized cooling tower with storm water or grey water evaporation

Controls

- Centralized limit for AC - 78 º F + Outside Air

- Outside air reset on heating with seatback

- Tenant leaves building  all systems shut off in apartment except refrigerator and plug loads

- BTU billing – flow meters?  Can NYSERDA pay for this?

- VFDs – Variable Frequency Drives

Envelope

- Good windows

- Insulation in the cavity

- Green roofing

- Appropriate exterior shading

Lighting and Appliances

- Energy Star everything

- Bi-level hallway

- Gearless elevator

- High efficiency potable water booster pumps

Extra

- Cogen unit?